## Slide 1
Building Energy and Carbon Rating and Labeling:
a Briefing
Surapong Chirarattananon
Joint Graduate School of Energy and Environment

## Slide 2
Rationale
An energy and carbon rating scheme helps promote the movement towards sustainable buildings by helping public and individuals in the identification and adopting more energy performing and low carbon buildings
A scientifically proven energy and carbon rating scheme can prove its own credibility.
Coupled with financial incentive to gain initial penetration, a good scheme will sustain itself.
Such scheme makes it clear to owners and everybody what constitutes energy efficient and low carbon systems and buildings and how cost-effective these are.

## Slide 3
Composition of a Building Energy Labeling Scheme
Thailand is accustomed to energy system performance based scheme for buildings, rather than prescription based requirements.
The 3 main systems are building envelope, air-conditioning, and lighting.
There is a scientific based energy efficiency indicator for each system that is directly related to energy consumption of the system.
Nominal energy consumption of the whole building can be derived from the value of the indicator of each system of a given building.

## Slide 4
Overall Thermal Transfer Value – OTTV
The indicator for building envelope is called OTTV.
For commercial buildings, the OTTV is calculated as cooling coil load due to heat gain across a building envelope per area of the envelope and is expressed as
(1-WWR)(Uw)(TDeq)+(WWR)(Uf)(∆T)+(WWR)(SHGC)(ESR)
In Thailand, an OTTV formulation is developed each for office, department store, and hotel type of building.

## Slide 5
OTTV VS LCC for Building Envelope with WWR = 0.3
Plots of LCC VS OTTV for WWR= 0.3
Overall Thermal Transfer Value – OTTV and its Life Cycle Cost (LCC)
From a study using different compositions of envelope configurations and compositions, the results show that higher OTTV leads to lower LCC.

## Slide 6
Combined air-side and water-side X kW/RFT
Energy Performance Requirements for Air-conditioning
Rated performance requirement of the whole A/C system is used (same requirements for all building types)
Chiller Y kW/RFT
Whole system performance = X+Y kW/RFT

## Slide 7
Energy Performance Requirements for Air-conditioning
Previous study with assistance from A/C system suppliers also shows that LCC is generally lower for higher system performance

## Slide 8
Energy Performance Requirements for Electric Lighting
Allowable rated power for lighting.
Category of building (1) Allowable rated power
(W/m2. of utilized area)
(a) Offices or educational buildings 14
(b) Department stores, retail stores, 18
shopping centers or hypermarket (2)
(c) Hotels, hospitals/convalescent homes 12
Lighting power budget applies to whole building (excluding car park) and allows for different requirements of different building types.

## Slide 9
Energy Performance Requirements for Electric Lighting
Previous studies on the use of different combinations of lighting devices show that LCC also decreases with increasing lighting energy performance (lower W/m2).

## Slide 10
Nominal (Electrical) Energy Consumption of the Whole Building
The nominal energy consumption of the whole building is obtained as a summation of adjusted rated consumption due to OTTV, air-conditioning, lighting, occupants, and equipment of each space in the building, Epa

## Slide 11
Nominal (Electrical) Energy Consumption of the Whole Building and Energy Performance Rating
The method has allowance for variations of occupancy density, building shape, deviation of operating schedule, and diversity of equipment use.
If a given building is to be rated for energy efficiency, the method based on rating the performance of each system to different levels and using the equation for obtaining its nominal whole building energy use can be applied.
In this case, the nominal consumption of a given building is compared to the nominal consumption of the same building with performance levels of all systems set to a common level.

## Slide 12
If the original nominal consumption is not larger than that of this latter case, the performance of the original building is rated to the given level.
With this method, a building is rated against its own potential and not against other buildings that may be different in many respects, such as density of people, size, configuration, equipment density, duration of use, etc.
Essentially, each building is energy rated by the performance of its three major building systems.
It is a straight forward step to extend this scheme to carbon rating.
Nominal (Electrical) Energy Consumption of the Whole Building and energy performance rating (cont.)

## Slide 13
Item | Office | Hotel | Hospital | Dept store | School | Hypermarket | Condominium | Misc.
AC energy/AC area, kWh.m-2.Y-1 | 131.7 | 172.0 | 155.4 | 361.9 | 122.1 | 210.4 | 168.1 | 265.9
Light energy/used area, kWh.m-2.Y-1 | 27.1 | 34.7 | 30.0 | 129.4 | 19.3 | 81.6 | 18.3 | 34.0
Total energy/used area, kWh.m-2.Y-1 | 146.4 | 173.3 | 148.8 | 556.0 | 93.9 | 394.6 | 118.3 | 139.6
AC area/total area, % | 65.7 | 66.9 | 54.5 | 85.9 | 26.6 | 69.8 | 47.3 | 19.7
AC energy/total energy, % | 59.1 | 66.4 | 56.9 | 55.9 | 34.6 | 37.2 | 67.2 | 37.6
Light energy/total energy, % | 18.5 | 20.0 | 20.2 | 23.3 | 20.5 | 20.7 | 15.5 | 24.4
OTTV, W.m-2 | 62.9 | 55.7 | 52.7 | 45.3 | 53.4 | 36.3 | 50.0 | 51.4
RTTV, W.m-2 | 28.4 | 23.4 | 30.6 | 20.9 | 33.8 | 22.9 | 17.4 | 21.0
AC performance, kW/RFT -split type -window type -package type -chillers | 1.51 1.83 1.38 1.02 | 1.64 1.76 na 1.09 | 1.59 na 1.30 0.75 | 1.48 na 1.06 0.71 | 1.51 2.03 na 1.07 | 0.20 1.45 na 2.08 | 0.20 na na na | na na na na
Experience of Energy Audit and System Performance Evaluation
Over 2,000 audits have been conducted with results shown.

## Slide 14
Conclusion
Thailand has more than 20 years of experience in theoretical and practical works on energy performance assessment of buildings.
The building energy code of Thailand is based on rated energy performance of three major systems of a building.
The building energy performance assessment used can be extended to form a energy and carbon rating of a building.
The tool for assessment developed for assessing code compliance can be used also for such scheme.